## CSV
| Solar | Wind | Nuclear | Gas | Coal | Battery
Cap Cost 2020 | Solar PV w/ Single Axis Tracking | Onshore Wind – Large Plant Footprint: Great Plains Region | Advanced Nuclear (Brownfield) | Combined-Cycle 1x1x1, Single Shaft | 650 MW Net, Ultra-Supercritical Coal w/o Carbon Capture – Greenfield | Battery Energy Storage System
Line (Cap Cost 2020) | 24 | 20 | 11 | 8 | 1 | 18
| Lifetime_Solar | Lifetime_Wind | Lifetime_Nuclear | Lifetime_Gas | Lifetime_Coal | Lifetime_Battery
Lifetime | 30 | 25 | 40 | 25 | 40 | 10

## Cap cost 2020
Capital Costs and Performance Characteristics for Utility Scale Power Generating Technologies (eia.gov)
Table 2 — Cost & Performance Summary Table
Case No. | Technology | Description | Net Nominal Capacity (kW) | Net Nominal Heat Rate (Btu/Kwh) | Capital Cost ($/kW) | Fixed O&M Cost ($/kW-year) | Variable O&M Cost ($/MWh) | NOx (lb/MMBtu) | SO2 (lb/MMBtu) | CO2 (lb/MMBtu) | (Lifetime)
1 | 650 MW Net, Ultra-Supercritical Coal w/o Carbon Capture – Greenfield | 1 x 735 MW Gross | 650 | 8638 | 3676 | 40.58 | 4.5 | 0.06 | 0.09 | 206 | 40 | 1
2 | 650 MW Net, Ultra-Supercritical Coal 30% Carbon Capture | 1 x 769 MW Gross | 650 | 9751 | 4558 | 54.3 | 7.08 | 0.06 | 0.09 | 144 | 40 | 2
3 | 650 MW Net, Ultra-Supercritical Coal 90% Carbon Capture | 1 x 831 MW Gross | 650 | 12507 | 5876 | 59.54 | 10.98 | 0.06 | 0.09 | 20.6 | 40 | 3
4 | Internal Combustion Engines | 4 x 5.6 MW | 21 | 8295 | 1810 | 35.16 | 5.69 | 0.02 | 0 | 117 | 30 | 4
5 | Combustion Turbines – Simple Cycle | 2 x LM6000 | 105 | 9124 | 1175 | 16.3 | 4.7 | 0.09 | 0 | 117 | 40 | 5
6 | Combustion Turbines – Simple Cycle | 1 x GE 7FA | 237 | 9905 | 713 | 7 | 4.5 | 0.03 | 0 | 117 | 40 | 6
7 | Combined-Cycle 2x2x1 | GE 7HA.02 | 1083 | 6370 | 958 | 12.2 | 1.87 | 0.0075 | 0 | 117 | 40 | 7
8 | Combined-Cycle 1x1x1, Single Shaft | H Class | 418 | 6431 | 1084 | 14.1 | 2.55 | 0.0075 | 0 | 117 | 25 | 8
9 | Combined-Cycle 1x1x1, Single Shaft, w/ 90% Carbon Capture | H-Class | 377 | 7124 | 2481 | 27.6 | 5.84 | 0.0075 | 0 | 11.7 | 40 | 9
10 | Fuel Cell | 34 x 300 kW Gross | 10 | 6469 | 6700 | 30.78 | 0.59 | 0.0002 | 0 | 117 | 20 | 10
11 | Advanced Nuclear (Brownfield) | 2 x AP1000 | 2156 | 10608 | 6041 | 121.64 | 2.37 | 0 | 0 | 0 | 40 | 11
12 | Small Modular Reactor Nuclear Power Plant | 12 x 50-MW Small Modular Reactor | 600 | 10046 | 6191 | 95 | 3 | 0 | 0 | 0 | 40 | 12
13 | 50-MW Biomass Plant | Bubbling Fluidized Bed | 50 | 13300 | 4097 | 125.72 | 4.83 | 0.08 | <0.03 | 206 | 40 | 13
14 | 10% Biomass Co-Fire Retrofit | 300-MW PC Boiler | 30 | 0.015 | 705 | 25.57 | 1.9 | 0%–20% | -0.08 | -0.08 | 20 | 14
15 | Geothermal | Binary Cycle | 50 | N/A | 2521 | 128.544 | 1.16 | 0 | 0 | 0 | 40 | 15
16 | Internal Combustion Engines – Landfill Gas | 4 x 9.1 MW | 35.6 | 8513 | 1563 | 20.1 | 6.2 | 0.02 | 0 | 117 | 30 | 16
17 | Hydroelectric Power Plant | New Stream Reach Development | 100 | N/A | 5316 | 29.86 | 0 | 0 | 0 | 0 | 50 | 17
18 | Battery Energy Storage System | 50 MW ¦ 200 MWh | 50 | N/A | 1389 (347 $/kWh) | 24.8 | 0 | 0 | 0 | 0 | 10 | 18
19 | Battery Energy Storage System | 50 MW ¦ 100 MWh | 50 | N/A | 845 (423 $/kWh) | 12.9 | 0 | 0 | 0 | 0 | 10 | 19
20 | Onshore Wind – Large Plant Footprint: Great Plains Region | 200 MW ¦ 2.82 MW WTG | 200 | N/A | 1265 | 26.34 | 0 | 0 | 0 | 0 | 25 | 20
21 | Onshore Wind – Small Plant Footprint: Coastal Region | 50 MW ¦ 2.78 MW WTG | 50 | N/A | 1677 | 35.14 | 0 | 0 | 0 | 0 | 25 | 21
22 | Fixed-bottom Offshore Wind: Monopile Foundations | 400 MW ¦ 10 MW WTG | 400 | N/A | 4375 | 110 | 0 | 0 | 0 | 0 | 25 | 22
23 | Concentrating Solar Power Tower | with Molten Salt Thermal Storage | 115 | N/A | 7221 | 85.4 | 0 | 0 | 0 | 0 | 30 | 23
24 | Solar PV w/ Single Axis Tracking | 150 MWAC | 150 | N/A | 1313 | 15.25 | 0 | 0 | 0 | 0 | 30 | 24
25 | Solar PV w/ Single Axis Tracking + Battery Storage | 150 MWAC Solar 50 MW ¦ 200 MWh Storage | 150 | N/A | 1755 | 31.27 | 0 | 0 | 0 | 0 | 30 | 25